PARAMETROS  GENERALES  DE VARIADOR HF Los simbolos le indican:

×  Funcion modificable con motor parado.

√  Funcion modificable con motor parado o en marcha.

△  Funcion que no se puede cambiar.

○   Valores del motor.

Appendix 2           Codigo Zoom Table

| Tipo | Codigo | Definicion | Rango Programable | Valor de Fabrica | Note |
| --- | --- | --- | --- | --- | --- |
| Basic Parameters | F100 | Contraseña que permite modificar valores | 0～9999 | 8 | √ |
|  | F101 | Funcion no Modificable |  |  |  |
|  | F102 | Inverter Rated Current (A) |  | Subject to inverter’s model | △ |
|  | F103 | Inverter’s Power (KW) | 0.20～110.0 | Power value of this inverter | △ |
|  | F104 | Funcion no Modificable |  |  |  |
|  | F105 | Software Edition Serial No. |  | Subject to software edition | △ |
|  | F106 | Inverter’s Input Voltage Type | 1:single phase 3:three phase | Subject to inverter’s model | △ |
|  | F107 | Inverter’s Rated Input-Voltage (V) | 220 or 380 | Subject to inverter’s model | △ |
|  | F108～F110 | Funcion no Modificable |  |  |  |
|  | F111 | Frecuencia Maxima (Hz) | F112～400.0 | 60.00 | × |
|  | F112 | Frecuencia Minima (Hz) | 0.00～MIN（50.00，F111） | 0.00 | × |
|  | F113 | Digital Setting Frequency (Hz) | F112～F111 | 50.00 | √ |
|  | F114 | 1st Tiempo de Aceleracion (S) | 0.1～3000 | 20.0 | √ |
|  | F115 | 1st Tiempo de Desaceleracion (S) | 0.1～3000 | 20.0 | √ |
|  | F116 | 2nd Tiempo de Aceleracion (S) | 0.1～3000 | 20.0 | √ |
|  | F117 | 2nd Tiempo de Desaceleracion (S) | 0.1～3000 | 20.0 | √ |
|  | F118 | Turnover Frequency（Hz） | 50.00～400.0 | 50.00 | × |
|  | F119 | Latent Frequency（Hz） | F112～F111 | 5.00 | √ |
|  | F120 | Tiempo de descanzo entre cambio de sentido de giro | 0.0～3000 | 2.0 | √ |
|  | F121 | Stop Mode Selection | 0: stop by deceleration time 1: free stop | 0 | × |
|  | F122 | Reverse Prohibitted | 0: nulo 1:valido | 0 | × |
|  | F123 | Funcion no Modificable |  |  |  |
|  | F124 | Salto de Frecuencia (Hz) | F112～F111 | 5.00 | √ |
|  | F125 | Tiempo de Salto de Desaceleracion (S) | 0.1～3000 | 20.0 | √ |
|  | F126 | Tiempo de Salto de Desaceleracion (S) | 0.1～3000 | 20.0 | √ |
|  | F127 | Skip Frequency A (Hz) | 0.00～F111 | 0.00 | × |
|  | F128 | Skip Area for Point A（Hz） | 0.00～5.00 | 0.00 | × |
|  | F129 | Skip Frequency B (Hz) | 0.00～F111 | 0.00 | × |
| Tipo | Codigo | Definicion | Rango Programable | Valor de Fabrica | Note |
| Basic Parameters | F130 | Skip Area for B Point (Hz) | 0.00～5.00 | 0.00 | × |
|  | F131 | Displays Eleccion del parametro a visualizar de fabrica muestra todos con el valor prefijado seleccion en marcha con flechas | 1～127 1: Frequency 2:Rotate Speed 4:Count Value 8:Output Current 16:Codigo Editting 32: Output Voltage 64:Linear Velocity 127: Display All | 127 | √ |
|  | F132 | Number of motor pole pairs rpm del motor se lee en “F131” op 2 | 1～6 | 2 diseño en 50hz, valores aprox 1=2870 2=1425 3=960 4=730 5=560 6=475 | × |
|  | F133 | Driven system’s drive ratio | 0.1～100.0 | 1.0 | × |
|  | F134 | Transmission-wheel radius (m) | 0.001～1.000 | 0.001 | × |
|  | F135～F138 | Funcion no Modificable |  |  |  |
|  | F139 | Whether auto start after reconnected or malfunction | 0:Nulo 1:Valido | 0 | × |
|  | F140～F159 | Funcion no Modificable |  |  |  |
|  | F160 | Volver a la programacion original | 0:Not restoring Valor de Fabrica 1: Recuperar Valor de Fabrica | 0 | × |
| Running control parameters | F200 | Control de Marcha | 0:Keypad Control/485 Communication Control 1: Terminal Control 2: Computer remote control | 0 Marcha parada controlada : 0= mediante el teclado 1= mediante switch externo Borne: CM=Comun OP6= Llave de marcha OP7= Llave de contramarcha OP8= Pulsador de reset en caso de falla | × |
|  | F201 | stop/reset Key Function Scope | 0: valido only with keypad control 1:valido in all control modes 2: valido with keypad and terminal 3-line control, direction pulse controlstart/stop, code speed control and computer remote control | 0 | × |
|  | F202-3 | Funcion no Modificable |  |  |  |
|  | F204 | Modo Basico de Velocidad de Control | 0: Digital frequency setting, keypad and terminal UP & DOWN setting, not saving settings after power failure 1: Digital frequency setting, keypad and terminal UP & DOWN setting, saving settings after power failure 2: Multi speed control 3: Analog channel 1 (AN1) speed control 4:Analog channel 2(AN2) speed control 5:Coumpound speed control 1:K1*AN1+K2*AN2 6:Coumpound speed control 2:K1*AN1－K2*AN2 7:Speed control with pulse frequency given 8:Code speed control 9:Coumpound speed control 3:K1*AN1+K2*(AN2-5V) 10:Keypad potentiameter speed control selection Note3 | 0 Asignar el valor: 0 para operar desde el teclado ó 3 para utilizar el variador con un potenciometro externo, entre los bornes (10V-AN1-GND) | × |
| Tipo | Codigo | Definicion | Rango Programable | Valor de Fabrica | Note |
| Running Control parameters | F205-6 | Funcion no Modificable |  |  |  |
|  | F207 | Keypad direction set | 0: Forward 1: Reverse | 0 | √ |
|  | F208 | Terminal control mode | 0: 2-line 1 1: 2-line 2 2: 3-line 1 3: 3-line 2 4: Start/stop controlled by direction pulse control | 0 | × |
|  | F209 | Cpeed-Change Control | 0: No adjustment is allowed for speeds 1: Adjustment is allowed for speeds | 0 | × |
|  | F210 | Tipos de Velocidad | 0: Multi speed running 1: Auto circulation running 2: 8th speed running | 0 | × |
|  | F211 | Auto Circulation Running Speed Selection | 2～7 | 7 | × |
|  | F212 | Auto Circulation Running Times Selection | 0～9999 | 0 | √ |
|  | F213 | Free Running Selection after Auto Circulation Running ends | 0: Stop 1: Keep running at last speed | 0 | √ |
|  | F214 | k1 | 0.0～10.0 | 1.0 | √ |
|  | F215 | k2 | 0.0～10.0 | 1.0 | √ |
|  | F216-20 | Funcion no Modificable |  |  |  |
|  | F221 | Counting Sub-frequencies | 1～1000 | 1 | × |
|  | F222 | Setting Counting Times | F224～9999 | 1 | × |
|  | F223 | Funcion no Modificable |  |  |  |
|  | F224 | Designating Counting Times | 1～F222 | 1 | × |
|  | F225-29 | Funcion no Modificable |  |  |  |
|  | F230 | Frequency Adjust Step Length (Hz) | 0.01～1.00 | 0.01 | × |
|  | F231-60 | Funcion no Modificable |  |  |  |
| Multi-Speed Parameters | F300 | 1st Speed Running Direction | 0: Forward 1: Reverse | 0 | √ |
|  | F301 | 1st Speed Tiempo de Aceleracion | 0.1～3000 | 20.0 | √ |
|  | F302 | 1st Speed Running Frequency | F112～F111 | 5.00 | √ |
|  | F303 | 1st Speed Running Time | 0.1～3000 | 20.0 | √ |
|  | F304 | 1st Speed Tiempo de Desaceleracion | 0.1～3000 | 20.0 | √ |
|  | F305 | 1st Speed Stop/Wait Time | 0.0～3000 | 0.0 | √ |
| Tipo | Codigo | Definicion | Rango Programable | Valor de Fabrica | Note |
| Multi-Speed Parameters | F306 | 2nd Speed Running Direction | 0: Forward 1: Reverse | 1 | √ |
|  | F307 | 2nd Speed Tiempo de Aceleracion | 0.1～3000 | 20.0 | √ |
|  | F308 | 2nd Speed Running Frequency | F112～F111 | 10.00 | √ |
|  | F309 | 2nd Speed Running Time | 0.1～3000 | 20.0 | √ |
|  | F310 | 2nd Speed Tiempo de Desaceleracion | 0.1～3000 | 20.0 | √ |
|  | F311 | 2nd Speed Stop/Wait Time | 0.0～3000 | 0.0 | √ |
|  | F312 | 3rd Speed Running Direction | 0: Forward 1: Reverse | 0 | √ |
|  | F313 | 3rd Speed Tiempo de Aceleracion | 0.1～3000 | 20.0 | √ |
|  | F314 | 3rd Speed Running Frequency | F112～F111 | 15.00 | √ |
|  | F315 | 3rd Speed Running Time | 0.1～3000 | 20.0 | √ |
|  | F316 | 3rd Speed Tiempo de Desaceleracion | 0.1～3000 | 20.0 | √ |
|  | F317 | 3rd Speed Stop/Wait Time | 0.0～3000 | 0.0 | √ |
|  | F318 | 4th Speed Running Direction | 0: Forward 1: Reverse | 1 | √ |
|  | F319 | 4th Speed Tiempo de Aceleracion | 0.1～3000 | 20.0 | √ |
|  | F320 | 4th Speed Running Frequency | F112～F111 | 20.00 | √ |
|  | F321 | 4th Speed Running Time | 0.1～3000 | 20.0 | √ |
|  | F322 | 4th Speed Tiempo de Desaceleracion | 0.1～3000 | 20.0 | √ |
|  | F323 | 4th Speed Stop/Wait Time | 0.0～3000 | 0.0 | √ |
|  | F324 | 5th Speed Running Direction | 0: Forward 1: Reverse | 0 | √ |
|  | F325 | 5th Speed Tiempo de Aceleracion | 0.1～3000 | 20.0 | √ |
|  | F326 | 5th Speed Running Frequency | F112～F111 | 25.00 | √ |
|  | F327 | 5th Speed Running Time | 0.1～3000 | 20.0 | √ |
|  | F328 | 5th Speed Tiempo de Desaceleracion | 0.1～3000 | 20.0 | √ |
|  | F329 | 5th Speed Stop/Wait Time | 0.0～3000 | 0.0 | √ |
|  | F330 | 6th Speed Running Direction | 0: Forward 1: Reverse | 0 | √ |
|  | F331 | 6th Speed Tiempo de Aceleracion | 0.1～3000 | 20.0 | √ |
|  | F332 | 6th Speed Running Frequency | F112～F111 | 30.00 | √ |
|  | F333 | 6th Speed Running Time | 0.1～3000 | 20.0 | √ |
|  | F334 | 6th Speed Tiempo de Desaceleracion | 0.1～3000 | 20.0 | √ |
|  | F335 | 6th Speed Stop/Wait Time | 0.0～3000 | 0.0 | √ |
| Tipo | Codigo | Definicion | Rango Programable | Valor de Fabrica | Note |
| Multi-Speed Parameters | F336 | 7th Speed Running Direction | 0: Forward 1: Reverse | 0 | √ |
|  | F337 | 7th Speed Tiempo de Aceleracion | 0.1～3000 | 20.0 | √ |
|  | F338 | 7th Speed Running Frequency | F112～F111 | 35.00 | √ |
|  | F339 | 7th Speed Running Time | 0.1～3000 | 20.0 | √ |
|  | F340 | 7th Speed Tiempo de Desaceleracion | 0.1～3000 | 20.0 | √ |
|  | F341 | 7th Speed Stop/Wait Time | 0.0～3000 | 0.0 | √ |
|  | F342 | Compound Speed Control Selection | 0: Not Allowed 1:Allowed | 0 | √ |
|  | F343 | Compound Speed Control Mode Selection | 0:Multi Speed Running Frequency + F344 Setting Value 1: Multispeed Running Frequency + AN2 Channel Analog Value | 0 | √ |
|  | F344 | Digital Frequency Setting for Compound Speed Control(Hz) | 0.00～20.00 | 0.00 | √ |
|  | F345-60 | Funcion no Modificable |  |  |  |
| Programmable Input/Output Teminal Parameters | F400-7 | Funcion no Modificable |  |  |  |
|  | F408 | OP1 Function Setting | 0: No function 1: Multi speed terminal 1 2: Multi-speed terminal 2 3: Multi-speed terminal 3 4: Reset 5: Free stop 6: Funcion no Modificable 7: External Emergency Stop 8: Acceleration / Deceleration Prohibited 9: JOGF Salto Forward 10:JOGR Salto Reverse 11:UP Frequency increase by degrees 12:DOWN Frequency decrease by degrees 13: FWD 14: REV 15:3-Line Input “Ｘ” Teminal 16: Acceleration/Deceleration Switchover 17: Malfunction with peripheral equipment 18: Code speed control input 19: Close loop switched to open loop 20: Compound channel speed control to single channel speed control 21: Teminal Counting 22: Counting Value Resetting 23: Pulse Frequency Input (valido only for OP1) | 9 | × |
|  | F409 | OP2 Function Setting |  | 1 | × |
|  | F410 | OP3 Function Setting |  | 2 | × |
|  | F411 | OP4 Function Setting |  | 3 | × |
|  | F412 | OP5 Function Setting |  | 7 | × |
|  | F413 | OP6 Function Setting |  | 13 | × |
|  | F414 | OP7 Function Setting |  | 14 | × |
|  | F415 | OP8 Function Setting |  | 4 | × |
| Tipo | Codigo | Definicion | Rango Programable | Valor de Fabrica | Note |
| Programmable Input/Output Teminal Parameters | F416 | Relay Output Function Selection | 0: No function 1: Inverter malfunction protection 2: Over latent frequency 3: Free stop 4: Inverter in running 5: In DC braking 6: Swich indication of Acceleration/Deceleration 7: Reaching set counting value 8:Reaching designated counting value 9: Overload early warning signal 10: Recerve 11: Recerve 12: Recerve 13: Recerve | 1 | × |
|  | F417 | OUT Terminal Output Function Selection |  | 4 | × |
|  | F418 | FM Output Function Selection | 0:Indicating output frequency value 1: Indicating output current value | 0 | √ |
|  | F419 | FM Output Calibration (％) | 0～200 | 100 | √ |
|  | F420 | IM (FM) Output Range Selection | 0:b0～20mA（0～10V） 1: 4～20mA（2～10V） | 0 | √ |
|  | F421-60 | Funcion no Modificable |  |  |  |
| V/F Control Parameters | F500 | Slip Compensation | 0.00～0.08 | 0.03 | × |
|  | F501 | V/F Curve Control Mode CURVA DE ARRANQUE PREFIJADA | 0: Straight line 1: Polygonal line 2: Square | 0 1 NORMAL 2 ALTO TORQUE 3 BAJO TORQUE | × |
|  | F502 | Torque Promotion（％） AJUSTE DEL TORQUE en baja velocidad | 1～MIN（15，F506） | 5 rango de 1 a 15 | × |
|  | F503-4 | Funcion no Modificable |  |  |  |
|  | F505 | User-Defined Frequency Point１(Hz) | F112～F507 | 10.00 | × |
|  | F506 | User-Defined Voltage Point１(％) | F502～MIN(100，F508) | 30 | × |
|  | F507 | User-Defined Frequency Point 2 (Hz) | F505～F118 | 20.00 | × |
|  | F508 | User-Defined Voltage Point 2 (％) | F506～MIN(100，F509) | 40 | × |
|  | F509 | Corresponding Output Voltage of Turnover frequency (％) | F508～100 | 100 | × |
|  | F510 | Funcion no Modificable |  |  |  |
|  | F511 | Auto Voltage Adjusting | 0: Not adjuting 1:Adjusting | 0 | × |
|  | F512 | Carrier Wave Frequency Setting (kHz) | 1～subject to inverter’s setting value | Subject to inverter’s setting value | × |
| Tipo | Codigo | Definicion | Rango Programable | Valor de Fabrica | Note |
| V/F Control Parameters | F513 | Randum Carrier Wave Selection | 0: Not allowed 1:Allowed | 1 | × |
|  | F514 | DC Braking Function Selection | 0: Not allowed 1: Braking during start 2: Braking during stop 3: Braking for Start＋stop | 0 | × |
|  | F515 | Initial Frequency for DC Braking (Hz) | 0.00～5.00 | 5.00 | √ |
|  | F516 | DC Braking Current (％) | 0～150 | 100 | √ |
|  | F517 | Start Braking Duration (S) | 0.0～10.0 | 5.0 | √ |
|  | F518 | Stop Braking Duration (S) | 0.0～10.0 | 5.0 | √ |
|  | F519 | Energy Consumption Braking Ratio (％) | 0～100 | 50 | × |
|  | F520-4 | Funcion no Modificable |  |  |  |
|  | F525 | Stalling Adjusting Function Selection | 0: Not allowed 1:Allowed | 0 | × |
|  | F526 | Stalling Current Adjusting(％) | 120～200 | 160 | × |
|  | F527 | Stalling Voltage Adjusting(％) | 120～200 | 140 | × |
|  | F528-60 | Funcion no Modificable |  |  |  |
| PI Adjusting ParametersPI12-1与指定计数次数0000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000 | F600 | PI Adjusting Function Selection | 0: Not allowed 1:Allowed | 0 | × |
|  | F601 | PI Adjustment Given Channel Selection | 0: Digit provided 1: AN1 channel given 2: AN2 channel given | 0 | × |
|  | F602 | PI Adjustment Digit Provided (V) | 0.00～10.00 | 5.00 | × |
|  | F603 | PI Adjustment Feedback Channel Selection | 0: AN1 channel feedback 1: AN2 channel feedback 2: OP1 pulse channel feedback | 0 | × |
|  | F604 | Min PI Setting Analog (V) | 0.00～F606 | 0.00 | × |
|  | F605 | Corresponding Feedback Quantity for Min PI Setting Analog (V) | 0.00～10.00 | 0.00 | × |
|  | F606 | Max PI Setting Analog (V) | F604～10.00 | 10.00 | × |
|  | F607 | Corresponding Feedback Quantity for Max PI Setting Analog (V) | 0.00～10.00 | 10.00 | × |
|  | F608 | Proportion Gain | 1～1000 | 100 | √ |
|  | F609 | Integration Time (S) | 0.1～10.0 | 0.1 | √ |
|  | F610 | Sampling Cycle (S) | 0.1～10.0 | 0.1 | √ |
| Tipo | Codigo | Definicion | Rango Programable | Valor de Fabrica | Note |
| PI Adjusting ParametersPI12-1与指定计数次数0000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000 | F611 | PI Adjusting Precision (％) | 0～20 | 5 | √ |
|  | F612 | PI Adjusting Polarity | 0:Negative feedback adjusting 1:Positive feedback adjusting | 0 | × |
|  | F613-60 | Funcion no Modificable |  |  |  |
| Timing Control & Definable Protection Parameters | F700 | Selection of Free Stop Mode | 0: Immediate stop 1: Delayed stop | 0 | × |
|  | F701 | Delay-time for Free Stop and Programmable Output Terminal Action (S) | 0.0～60.0 | 0.0 | × |
|  | F702 | Fan Control Selection (valido only for 18.5～110KW inverter) | 0: Fan running controlled by temperature 1: Fan running not controlled by temperature | 0 | × |
|  | F703-4 | Funcion no Modificable |  |  |  |
|  | F705 | Times Allowed for Repeated Auto Start | 0～5 | 3 | × |
|  | F706 | Interval between Repeated Auto Start (S) | 0.0～10.0 | 3.0 | × |
|  | F707-8 | Funcion no Modificable |  |  |  |
|  | F709 | Undervoltage Protection Value (V) | 200～420 | Subject to inverter’s model | △ |
|  | F710-14 | Funcion no Modificable |  |  |  |
|  | F715 | Overload Adjusting Gain | 0～1000 | Debugging value | ○ |
|  | F716 | Inverter Overload Coefficient (％) | 150～180 | Debugging value | ○ |
|  | F717 | Motor Overload Coefficient (％) | 20～120 | Debugging value | ○ |
|  | F718-19 | Funcion no Modificable |  |  |  |
|  | F720 | Third Malfunctin Type by Counting Backward | 0: No malfunction 1: Acceleration overcurrent 2: Deceleration overcurrent 3: Constant speed overcurrent 4: Acceleration overvoltage 5: Deceleration overvoltage 6: Constant speed overvoltage 7: Undervoltage 9: Inverter overloading 10: Motor overloading 11: Over temperature 12:Usar con Contraseña error/serious external interference 13: Out-phase 15: Imergency stop 19:Galvanoscopy malfunction 21: Malfunction with peripheral equipment |  | △ |
|  | F721 | Second Malfunctin Type by Counting Backward |  |  |  |
|  | F722 | Type of the Latest Malfunction |  |  |  |
| Tipo | Codigo | Definicion | Rango Programable | Valor de Fabrica | Note |
| Timing Control & Settable Protection Parameters | F723 | Malfunction Frequency of the Latest Malfunction (Hz) |  |  | △ |
|  | F724 | Malfunction Current of the Latest Malfunction (A) |  |  | △ |
|  | F725 | Malfunction Voltage of the Latest Malfunction (V) |  |  | △ |
|  | F726-60 | Funcion no Modificable |  |  |  |
| Analog Parameters | F800 | Min Input of Analog (V) | 0.00～MIN(F801,10.00) | 0.00 | √ |
|  | F801 | Max Input of Analog (V) | MAX（0.00，F800）～10.00 | 10.00 | √ |
|  | F802-06 | Funcion no Modificable |  |  |  |
|  | F807 | VELOCIDAD MINIMA CON POTENCIOMETRO (Hz) | F112～F111 | 0.00 | √ |
|  | F808 | VELOCIDAD MAXIMA CON POTENCIOMETRO (Hz) | F112～F111 | 50.00 | √ |
|  | F809 | Max Input Pulse Frequency (Hz) | 0～9999 | 5000 | × |
|  | F810 | Corresponding Frequency of Max Input Pulse Frequency (Hz) | 0.00～F111 | 50.00 | × |
|  | F811 | Wave-Filtering Time Constant (S) | 1.0～10.0 | 3.0 | √ |
|  | F812-60 | Funcion no Modificable |  |  |  |
| Communication Parameters | F900 | 485 Communication Interface Function Selection | 0: Computer 1:485 communication enclosure | 1 | × |
|  | F901 | Communication Address | 1～127: Inverter address | 1 | × |
|  | F902 | Whether to have odd/even | 0: No checkout 1: Odd 2: Even | 0 | × |
|  | F903 | Communication Baud rate (bit) | 1: 2400 2: 4800 3: 9600 4: 19200 | 3 | × |
|  | F904-60 | Funcion no Modificable |  |  |  |